## Slide 1: Debre Markos University Debre Markos Institute of Technology
School of Electrical and computer Engineering
Introduction to Power system
3. Physical Aspects of Overhead and Underground Transmission and Distribution System

## Slide 2: Introduction
Electric power can be transmitted or distributed either by means of underground cables or by overhead lines.
The underground cables are rarely used for power transmission due to two main reasons.
  Firstly, power is generally transmitted over long distances to load centers. Obviously, the installation costs for underground transmission will be very heavy.
  Secondly, electric power has to be transmitted at high voltages for economic reasons.
<number>

## Slide 3: Under ground cables
Is much more expensive than overhead system.
Has limited use for distribution in congested areas where safety and good appearances are the main considerations.
Overhead lines
Bare conductors are used and air acts as the insulation.
The necessary insulation between the conductors can be provided by adjusting the spacing between them.
<number>

## Slide 4
May be used to transmit or distribute electric power.
The successful operation of an overhead line depends to a great extent upon the mechanical design of the line.
While constructing an overhead line, it should be ensured that mechanical strength of the line is such so as to provide against the most probable weather conditions.
<number>

## Slide 5: The main components of an overhead line are:
Conductors
Supports
Insulators
Cross arms
<number>

## Slide 6
Conductors which carry electric power from the sending end station to the receiving end station.
Supports which may be poles or towers and keep the conductors at a suitable level above the ground.
Insulators which are attached to supports and insulate the conductors from the ground.
Cross arms which provide support to the insulators.
Miscellaneous items such as phase plates, danger plates, lightning arrestors, anti-climbing wires etc.
<number>

## Slide 7: Conductor materials
The conductor is one of the important item.
The conductor material used for transmission and distribution of electric power should have the following properties:
  High tensile strength in order to withstand mechanical stresses.
  Low specific gravity so that weight per unit volume is small.
  High electrical conductivity.
  Low cost so that it can be used for long distances.
<number>
Notes: <number>

## Slide 8: Commonly used conductor materials
The most commonly used conductor materials for overhead lines are:
  Copper,
  Aluminium,
  Steel-cored aluminium,
  Galvanized steel and cadmium copper.
The choice of a particular material will depend upon the cost, the required electrical and mechanical properties and the local conditions.
<number>
Notes: <number>

## Slide 9
<number>
Copper:
Copper is an ideal material for overhead lines owing to its high electrical conductivity and greater tensile strength
It is always used in the hard drawn form as stranded conductor. Although hard drawn decreases the electrical conductivity slightly yet it increases the tensile strength considerably
The merits of this metal as a line conductor are:
  It has a best conductivity in comparison to other metals.
    The conductivity of copper, however depends upon the percentage of impurities present in it, the more the impurities the lesser will be the conductivity.
    The conductivity of copper conductor also depends upon the method by which it has been drawn.

## Slide 10
  ii. It has higher current density, so for the given current rating, lesser cross-sectional area of conductor is required and hence it provides lesser cross-sectional area to wind loads
  iii. The metal is quite homogeneous
  iv. It has low specific resistance
  v. It is durable and has a higher scrap value
Aluminum:
Aluminum is cheap and light as compared to copper but it has much smaller conductivity and tensile strength
Next to copper aluminum is the conductor used in order of performance as far as the conductivity is concerned.
<number>

## Slide 11
<number>
Its merits and demerits are:
  It is cheaper than copper
  It is lighter in weight (the specific gravity of aluminum is lower than that of copper, i.e an aluminum conductor has almost one half the weight of equivalent copper conductor)
  It is second in conductivity (among the metals used for transmission). Commercial hard-down aluminum wire at standard temperature has approximately 60.6 % conductivity in comparison to standard annealed copper wire.
  For same ohmic resistance, its diameter is about 1.27 times that of copper.
  At higher voltages it causes less corona loss
  Since the diameter of the conductor is more, so it is subject to greater wind pressure due to which greater is the swing of the conductor and greater is the sag
  Since the conductors are liable to swing, so it requires larger cross arms

## Slide 12
<number>
  viii. As the melting point of the conductor is low , so the short circuit etc. will damage it .
ix. Joining of aluminum is much more difficult than that of any other material
In the modern overhead transmission system, bare aluminum conductors are used (for purpose of heat dissipation), to increase strength of aluminum conductors reinforced with a core of galvanized steel wires, which are classifies as:
AAC - All Aluminum Conductors
AAAC - All Aluminum Alloy Conductors
ACSR – Aluminum Conductors Steel Reinforced
ACAR - Aluminum Conductors Alloy Reinforced
1- Steel strands
2- Aluminum strands
ACSR

## Slide 13
<number>
Steel
No doubt it has got the greatest tensile strength, but it is least used for transmission of electrical energy as it has got high resistance.
Bare steel conductors are not used since, it deteriorates rapidly owing to rusting. Generally galvanized steel wires are used.
It has the following properties:
  i ) It is lowest in conductivity
  ii ) It has high internal reactance
  iii ) It is much subjected to eddy current and hysteresis loss
  iv ) In a damp atmosphere it is rusted
Hence its use is limited

## Slide 14: Cadmium Copper
Addition of 1% or 2% cadmium to copper
Increased tensile strength by 50% than pure copper
Conductivity reduced by 15% below that of pure copper
Economical for lines of small cross-section due to high cost of cadmium
<number>

## Slide 15
Line supports
The supporting structures for overhead line conductors are various types of poles and towers called line supports.
In general, the line supports should have the following properties
  High mechanical strength to withstand the weight of conductors and wind load etc.
  Light in weight without the loss of mechanical strength
  Cheap in cost and economical to maintain
  Longer life
  Easy accessibility of conductors for maintenance
The line supports used for transmission and distribution of electric power are of various types including:
  Wooden poles,
  Steel poles,
  R.C.C. Poles and
  Lattice steel towers.
<number>

## Slide 16
The choice of supporting structure for a particular case depends upon:
  Line span,
  Cross-sectional area,
  Line voltage,
  Cost and local conditions.
<number>

## Slide 17: 1. Wooden pole
These poles:
  Are made of seasoned wood (sal or chir)
  Are suitable for lines of moderate x-sectional area
  Relatively shorter spans, up to 50 metres.
Such supports are:
  Cheap,
  Easily available,
  Provide insulating properties
  Are widely used for distribution purposes in rural areas.
<number>

## Slide 18
The wooden poles generally tend to rot below the ground level, causing foundation failure.
In order to prevent this, the portion of the pole below the ground level is impregnated with preservative compounds like creosote oil.
Double pole structures of the ‘A’ or ‘H’ type are often used (See Fig. 3.1) to obtain a higher transverse strength than could be economically provided by means of single poles.
<number>

## Slide 19
The main objections to wooden supports are:
  Tendency to rot below the ground level
  Comparatively smaller life (20-25 years)
  Cannot be used for voltages higher than 20 KV
  Less mechanical strength and
  Require periodical inspection.
<number>
Notes: <number>

## Slide 20
Fig 3.1 wooden poles
<number>

## Slide 21
The steel poles are often used as a substitute for wooden poles.
They possess greater mechanical strength, longer life and permit longer spans to be used.
Such poles are generally used for distribution purposes in the cities.
This type of supports need to be galvanized or painted in order to prolong its life.
There are three types of steel poles,
  rail poles
  tubular poles and
  rolled steel joints
2. Steel pole
<number>

## Slide 22: 3. RCC pole
The reinforced concrete poles have become very popular as line supports in recent years.
They have greater mechanical strength, longer life and permit longer spans than steel poles.
Moreover, they give good outlook, require little maintenance and have good insulating properties.
The holes in the poles facilitate the climbing of poles and at the same time reduce the weight of line supports.
The main difficulty with the use of these poles is the high cost of transport owing to their heavy weight.
Therefore, such poles are often manufactured at the site in order to avoid heavy cost of transportation.
Fig. 3.2 shows R.C.C. poles for single and double circuit.
<number>

## Slide 23
Fig 3.2 RCC pole
Fig. 3.2 (i) shows a single circuit tower. However, at a moderate additional cost, double circuit tower can be provided as shown in Fig. 3.2 (ii).
<number>

## Slide 24
Reinforced Concrete Poles
<number>

## Slide 25: 4. Steel towers
In practice, wooden, steel and reinforced concrete poles are used for distribution purposes at low voltages, say up to 11 kV.
However, for long distance transmission at higher voltage, steel towers are invariably employed.
Steel towers
  have greater mechanical strength,
  longer life,
  can withstand most severe climatic conditions and permit the use of longer spans.
The risk of interrupted service due to broken or punctured insulation is considerably reduced owing to longer spans.
Tower footings are usually grounded by driving rods into the earth.
This minimizes the lightning troubles as each tower acts as a lightning conductor.
<number>

## Slide 26
single circuit tower b) double circuit tower
Fig 3.3 Steel Towers
<number>

## Slide 27: View of tubular Poles
<number>

## Slide 28: Transmission line (Steel tower)
<number>

## Slide 29: Transmission line (Steel tower)
<number>

## Slide 30: Transmission line (Steel tower)
<number>

## Slide 31: View of L.T. distribution system
<number>

## Slide 32: Distribution Transformer
<number>

## Slide 33: Sag and Tension in Overhead Lines
While erecting an overhead line, it is very important that conductors are under safe tension.
If the conductors are too much stretched between supports in a bid to save conductor material, the stress in the conductor may reach unsafe value and in certain cases the conductor may break due to excessive tension.
In order to permit safe tension in the conductors, they are not fully stretched but are allowed to have a dip or sag.
The difference in level between points of supports and the lowest point on the conductor is called sag.
Fig. below (i) shows a conductor suspended between two equivalent supports A and B.
The conductor is not fully stretched but is allowed to have a dip.
<number>

## Slide 34
The lowest point on the conductor is O and the sag is S. The following points may be noted:
  When the conductor is suspended between two supports at the same level, it takes the shape of catenary. However, if the sag is very small compared with the span, then sag-span curve is like a parabola.
  The tension at any point on the conductor acts tangentially. Thus tension TO at the lowest point O acts horizontally as shown in Fig. (ii).
  The horizontal component of tension is constant throughout the length of the wire.
<number>

## Slide 35
  The tension at supports is approximately equal to the horizontal tension acting at any point on the wire. Thus if T is the tension at the support B, then T = TO.
  Figure below shows a conductor suspended freely from two supports, which are at the same level and spaced L meter, takes the form of a catenary curve providing the conductor is perfectly flexible and conductor weight is uniformly distributed along its length.
<number>

## Slide 36
This is an important consideration in the mechanical design of overhead lines.
The conductor sag should be kept to a minimum in order to reduce the conductor material required and to avoid extra pole height for sufficient clearance above ground level.
Conductor Sag and Tension
<number>

## Slide 37
It is also desirable that tension in the conductor should be low to avoid the mechanical failure of conductor and to permit the use of less strong supports.
However, low conductor tension and minimum sag are not possible. It is because low sag means a tight wire and high tension, whereas a low tension means a loose wire and increased sag. Therefore, in actual practice, a compromise is made between the two.
<number>

## Slide 38: Calculation of Sag
In an overhead line, the sag should be so adjusted that tension in the conductors is within safe limits.
The tension is governed by
  conductor weight,
  effects of wind,
  ice loading and
  temperature variations.
<number>

## Slide 39
It is a standard practice to keep conductor tension less than 50% of its ultimate tensile strength i.e. minimum factor of safety in respect of conductor tension should be 2.
We shall now calculate sag and tension of a conductor when
  supports are at equal levels and
  supports are at unequal levels.
<number>

## Slide 40: When supports are at equal levels
Consider a conductor between two equilevel supports A and B with O as the lowest point as shown in Fig. . It can be proved that lowest point will be at the mid-span.
Let
l = Length of span
w = Weight per unit length of conductor
T = Tension in the conductor.
<number>

## Slide 41
Consider a point P on the conductor. Taking the lowest point O as the origin, let the co-ordinates of point P be x and y. Assuming that the curvature is so small that curved length is equal to its horizontal projection (i.e., OP = x), the two forces acting on the portion OP of the conductor are :
(a) The weight wx of conductor acting at a distance x/2 from O.
(b) The tension T acting at O.
<number>

## Slide 42
Equating the moments of above two forces about point O, we get,
The maximum dip (sag) is represented by the value of y at either of the supports A and B.
At support A,
<number>

## Slide 43: When supports are at unequal levels.
In hilly areas, we generally come across conductors suspended between supports at unequal levels. Fig. given below shows a conductor suspended between two supports A and B which are at different levels. The lowest point on the conductor is O.
<number>

## Slide 44
Let
l = Span length
h = Difference in levels between two supports
x1 = Distance of support at lower level (i.e., A) from O
x2 = Distance of support at higher level (i.e. B) from O
T = Tension in the conductor
If w is the weight per unit length of the conductor, then,
<number>

## Slide 45
<number>

## Slide 46: Effect of wind and ice loading
The above formulae for sag are true only in still air and at normal temperature when the conductor is acted by its weight only.
However, in actual practice, a conductor may have ice coating and simultaneously subjected to wind pressure.
The weight of ice acts vertically downwards i.e., in the same direction as the weight of conductor.
The force due to the wind is assumed to act horizontally i.e., at right angle to the projected surface of the conductor.
Hence, the total force on the conductor is the vector sum of horizontal and vertical forces as shown in Fig given in next slide.
<number>

## Slide 47
Total weight of conductor per unit length is
<number>

## Slide 48
When the conductor has wind and ice loading also, the following points may be noted :
The conductor sets itself in a plane at an angle θ to the vertical where
(ii) The sag in the conductor is given by :
(iii) The vertical sag = S cos θ
<number>

## Slide 49
Insulators
The overhead line conductors should be supported on the poles or towers in such a way that currents from conductors do not flow to earth through supports.
Provide Electrical insulation between line conductor and earthed structure under operating and overvoltage conditions
To act as a reliable mechanical link between the structure and the conductor and keep the mechanical integrity under normal operating and overload conditions.
The insulators are mainly made of either glazed, porcelain or toughened glass.
The dielectric strength of porcelain should be 15KV to 17KV for every one tenth inch thickness. Porcelain is mechanically strong, less affected by temperature and has minimum leakage problem.
<number>

## Slide 50
<number>
Toughened glass is also sometimes used for insulators because it has higher dielectric strength (35KV for one tenth inch thickness), But it has lower coefficient of thermal expansion. And it condenses moisture very easily (since those reasons it use is limited up to 33KV )
In general, the insulators should have the following desirable properties:
  High mechanical strength in order to withstand conductor load, wind load, etc
  High electrical resistance of insulator material in order to avoid leakage current to earth
  High relative permittivity of insulator material in order that dielectric strength is high
  The insulator material should be non-porous, free from impurities and cracks otherwise the permittivity will be lowered
  High ration of puncture strength to flashover

## Slide 51
<number>
Types of insulators
In overhead transmission lines, the conductors are suspended from a pole or a tower via insulators.
There are several types of insulators but the most commonly used are pin type, suspension type, strain insulator and shackle insulator
1. Pin type insulators
consist of a single or multiple shells adopted to be mounted on a spindle to be fixed to the cross arm of the supporting structure. Multiple shells are provided in order to obtain sufficient length of leakage.
There is a groove on the upper end of the insulator for housing the conductor. The conductor passes through this groove and is bound by the annealed wire of the same material as the conductor
Pin type insulators are used for transmission and distribution of electric power at voltages up to 33 kV. Beyond operating voltage of 33 kV, the pin type insulators become too bulky and hence uneconomical

## Slide 52
<number>
Cause of insulator failure
Insulators are required to withstand both mechanical and electrical stresses
The latter type is primarily due to line voltage and may cause the breakdown of the insulator
The electrical break down of the insulator can occur either by flash-over or puncture
Notes: Power system I, 2012
<number>

## Slide 53
<number>
In flash over, an arc occurs between the line conductor and insulator pin (i.e, earth) and the discharge jumps across the air gaps, following shortest distance
In case of flash-over, the insulator will continue to act in its proper capacity unless extreme heat produced by the arc destroys the insulator
In case of puncture, the discharge occurs from conductor to pin through the body of the insulator
When such breakdown is involved, the insulator is permanently destroyed due to excessive heat.
In practice, sufficient thickness of porcelain is provided in the insulator to avoid puncture by the line voltage
The ratio of puncture strength to flash over voltage is known as safety factor

## Slide 54
<number>
It is desirable that the value of safety factor is high so that flash-over takes place before the insulator gets punctured. For pin insulators, the value of safety factor is about 10
2. Suspension type insulators
The cost of pin type insulator increases rapidly as the working voltage is increases. Therefore, this type of insulator is not economical beyond 33 kV.
For high voltages (greater than 33 kV), it is a usual practice to use suspension type insulators shown in figure below.
They consists of a number of porcelain discs connected in series by metal links in the form of a string
The conductor is suspended at the bottom end of this string while the other end of the string is secured to the cross-arm of the tower. The number of discs in series would obviously depend upon the working voltage

## Slide 55
<number>

## Slide 56
<number>
Advantages
(i). Suspension type insulators are cheaper than pin type insulators for voltages beyond 33 kV
(ii). Each unit or disc of suspension type insulator is designed for low voltage, usually 11 kV. Depending upon the working voltage, the desired number of discs can be connected in series
(iii). If any one disc is damaged, the whole string does not become useless because the damaged disc can be replaced by the sound one
(iv). The suspension arrangement provides greater flexibility to the line. The connection at the cross arm is such that insulator string is free to swing in any direction and can take up the position where mechanical stress are minimum
(v). In case of increased demand on the transmission line, it is found more satisfactory to supply the greater demand by raising the line voltage than to provide another set of conductors. The additional insulation required for the raised voltage can be easily obtained in the suspension arrangement by adding the desired number of discs

## Slide 57
<number>
(vi). The suspension type insulators are generally used with steel towers. As the conductors run below the earthed cross-arm of the tower, therefore, this arrangement provides partial protection from lightning
3. Strain Insulators
When there is a dead end of the line or there is corner or sharp curve, the line is subjected to greater tension. In order to relive the line of excessive tension, strain insulators are used.
For low voltage lines (less than 11 kV), shackle insulators are used as strain insulators. However, for high voltage transmission lines, strain insulators consists of assembly of suspension insulators as shown in figure below.
The discs of strain insulators are used in the vertical plane. When the tension in line is exceedingly high, as at long river spans, two or more strings are used in parallel.

## Slide 58
<number>
4. Shackle Insulators
In early days, the shackle insulators were used as strain insulators. But now a day, they are frequently used for low voltage distribution line.
Such insulators can be used either in a horizontal position or a vertical position

## Slide 59
<number>
They can be directly fixed to the pole with a bolt or to the cross arm. Figure below shows a shackle insulator fixed to the pole. The conductor in the groove is fixed with a soft binding wire
Figure: Shackle insulator

## Slide 60: Potential distribution over a string of suspension insulators
A string of suspension insulators consists of a number of porcelain discs connected in series through metallic links.
The porcelain portion of each disc is in between two metal links. Therefore, each disc forms a capacitor C. This is known as mutual capacitance or self-capacitance.
If there were mutual capacitance alone, then charging current would have been the same through all the discs and consequently voltage across each unit would have been the same i.e., V/3 as shown in fig. (ii) in next slide.
However, in actual practice, capacitance also exists between metal fitting of each disc and tower or earth. This is known as shunt capacitance C1 as shown in fig. (iii) given in next slide.
<number>

## Slide 61
Due to shunt capacitance, charging current is not the same through all the discs of the string. Therefore, voltage across each disc will be different. Obviously, the disc nearest to the line conductor will have the maximum voltage. Thus V3will be much more than V2or V1.
<number>

## Slide 62
The following points may be noted regarding the potential distribution over a string of suspension insulators :
The voltage impressed on a string of suspension insulators does not distribute itself uniformly across the individual discs due to the presence of shunt capacitance.
The disc nearest to the conductor has maximum voltage across it. As we move towards the cross-arm, the voltage across each disc goes on decreasing.
The unit nearest to the conductor is under maximum electrical stress and is likely to be punctured. Therefore, means must be provided to equalize the potential across each unit.
If the voltage impressed across the string were d.c., then voltage across each unit would be the same. It is because insulator capacitances are ineffective for d.c.
<number>

## Slide 63: String Efficiency
Unequal potential distribution on the string of suspension insulators is undesirable and is usually expressed in terms of string efficiency.
The ratio of voltage across the whole string to the product of number of discs and the voltage across the disc nearest to the conductor is known as string efficiency i.e.,
<number>

## Slide 64
<number>
Fig. to the right shows the equivalent circuit for a 3-disc string. Let us suppose that self capacitance of each disc is C. Let us further assume that shunt capacitance C1is some fraction K of self capacitance i.e., C1= KC.
Starting from the cross-arm or tower, the voltage across each unit is V1,V2 and V3 respectively as shown.

## Slide 65
<number>
…………........(i)
……….….(ii)

## Slide 66
<number>
……………...…..(iii)

## Slide 67
Example:- In a 33 kV overhead line, there are three units in the string of insulators. If the capacitance between each insulator pin and earth is 11% of self-capacitance of each insulator, find
the distribution of voltage over 3 insulators and
string efficiency
<number>

## Slide 68
<number>

## Slide 69
<number>
Methods of equalizing potential
1. Selection of m (by using longer cross arm)
Design the units such that the direct capacitance between them is much greater than the capacitance to earth, a ratio of 6 to 10.
It means to have large value of m, but it is uneconomical to go beyond certain values of the length of the cross arm, it has been found that the value of m =10 is about the maximum which may be obtained.
2. Grading of Units
In this method, insulators of different dimensions are so chosen that each has a different capacitance.
The insulators are capacitance graded i.e. they are assembled in the string in such a way that the top unit has the minimum capacitance, increasing progressively as the bottom unit (i.e., nearest to conductor) is reached.
Since voltage is inversely proportional to capacitance, this method tends to equalize the potential distribution across the units in the string.
This method has the disadvantage that a large number of different-sized insulators are required, which is uneconomical and impractical
However, good results can be obtained by using standard insulators for most of the string and larger units for that near to the line conductor.

## Slide 70
<number>
3. Static shielding (using a guard ring)
In case of units grading we used units of different capacities, so that the flow of different currents through the respective units produce equal voltage drop.
In static shielding the idea is to cancel exactly the pin to tower charging currents so that the same current will flow through the units of identical capacities to produce equal voltage drop across each unit. [see fig. in the right ]

## Slide 71
<number>
Since identical units are being used their mutual capacities are equal. Similarly the ground capacitances are equal.
The design of the ring should be such that this gives rise to the capacitances which will cancel exactly the charging current in that particular section, such that
Where V is the operating voltage and Cn is the capacitance between the guard ring and the pin of the nth unit
Let V = kv where k is the number of units used. Then

## Slide 72
<number>
In order to increase the string efficiency, guard ring serves two purposes:
(i). Equalization of voltage drop across the units, and
(ii). When used with arcing horn (which is fixed at the top end of the string) it protects the insulator string from flashover whenever an over voltage (under normal or abnormal condition) appears between the tower structure and the power conductor.
Whenever a transmission line is seen through the areas where there is lot of smoke or chemical industry or where the frequency of lighting stroke is large, special design insulator are normally used.

## Slide 73
<number>
Example 1
Determine the maximum voltage that the string of the suspension insulator in figure below can withstand if the maximum voltage per unit is 17.5 kV.
Solution
Let the voltages across the various units be E1, E2, and E3 as shown, such that E = E1+E2+E3 where E is the desired withstand voltage of the string.

## Slide 74
<number>
Applying Kirchhoff’s current law at A

## Slide 75
<number>
Example 2
A string of eight suspension insulators is to be fitted with a guard ring. If the pin to earth capacitances are all equal to C, find the values of line to pin capacitances that would give a uniform voltage distribution over the string

## Slide 76
<number>
Solution
For voltage distribution to be uniform (see figure above)

## Slide 77
<number>

## Slide 78
Reading Assignment
      Cable line
      Types of Cables
      Current Rating of Cables
<number>