## Slide 1: Debre Markos University Debre Markos Institute of Technology
School of Electrical and computer Engineering
Introduction to Power system
1.6 Substations
<number>
Notes: <number>

## Slide 2
Substations are part of the power system where voltage level is changed or switching is being done.
Substations also serve the following functions;
Substations serve as sources of energy supply for the local areas of distribution in which these are located.
The energy transmitted at high voltage from the generating stations is reduced to low voltage for local distribution.
Some substations are simply switching stations where different connections between various transmission lines are made. Switching is done for maintenance purpose or disconnection of line at the time of fault.
1.6. Substations
<number>
Notes: <number>

## Slide 3
Protective devices are installed at the substations to disconnect equipment or circuit in the event of fault.
Voltage on the outgoing distribution feeders can be regulated at the substation.
A substation is convenient place for installing shunt capacitors at the end of the transmission line to improve the power factor and make measurements to check the operation of the various parts of the power system. An Aerial view of substation is shown in Figure below.
<number>
Notes: <number>

## Slide 4
Figure . Aerial View of a Substation.
<number>
Notes: <number>

## Slide 5
The substations may be classified in numerous ways such as on the basis of
(i) Nature of duties
(ii) Service rendered
(iii) Operating voltage
(iv) Importance
(v) Design
Classification of Substations
<number>
Notes: <number>

## Slide 6
Classification of Substations on the Basis of Nature of Duties
The substations, on the basis of nature of duties, may be classified into the following three categories:
a) Generating Substations or Step-Up Substations
These substations are associated with generating station. The terminal voltage of the synchronous generator (3.3 to 33 kV) is stepped up to high primary transmission voltage (220 or 500 kV) to reduce the size of conductor and the line losses.
<number>
Notes: <number>

## Slide 7
b) Primary Grid Substations
Such substations are located at suitable load centers along the primary transmission lines.
In these substations, the primary transmission voltage is stepped down to different suitable secondary transmission voltages.
The secondary transmission lines are carried over to the secondary substations situated at the load centers where the voltage is further stepped down to primary distribution voltages (11kV).
<number>
Notes: <number>

## Slide 8
c) Distribution Substations
Such substations are located at the load centers, where the primary distribution voltage is stepped down to secondary distribution voltage (11kV/400V). These substations feed the consumers through a network of distribution and service lines.
Classification of Substations Based on Service Rendered
The substations, according to service rendered are:
i) Transformer Substations
Transformers are installed on such substations to change the voltage level as per needs.
ii) Switching Substations
These substations are meant for switching operation of power lines without transforming the voltage. At such substations different connections are made between various transmission lines.
<number>
Notes: <number>

## Slide 9
iii) Converting Substations
Such substations are meant for either converting AC to DC or vice-versa or converting frequency from higher to lower or vice-versa.
Classification of Substations Based of Operating Voltage
The substations, according to operating voltage, may be categorized as follows;
High Voltage Substations (HV Substations)
These are the substations in which operating voltage between11 kV and 66 kV.
Extra High Voltage Substations (EHV Substations)
These are the substations in which operating voltage between 132 kV and 400 kV.
Ultra High Voltage Substations (UHV Substations)
These are the substations in which operating voltage is above 400 kV.
<number>
Notes: <number>

## Slide 10
Classification of Substations on The Basis of Importance
1) Grid Substations
These are the substations from where bulk power is transmitted from one point to another point in the grid. These are important because any disturbance in these substations may cause the failure of the grid.
2) Town Substation
These substations step-down the voltages at 33/11 kV for further distribution in the towns and any failure in such substations results in the failure of supply for whole of the town.
<number>
Notes: <number>

## Slide 11
Classification of Substations on the Basis of Design
Indoor Type Substations
In such substations the apparatus is installed within the substation building. Such substations are usually for a voltage up to 11 kV but can be erected for the 33 kV and 66 kV when the surrounding atmosphere is contaminated with impurities such as metal corroding gases and fumes, conductive dust etc.
Outdoor Substations
These substations are further subdivided into:
<number>
Notes: <number>

## Slide 12
a) Pole Mounted Substations
Such substations are erected for distribution of power in localities. Single stout pole or H-pole and 4-pole structures with suitable platforms are employed for transformers of capacity up to 25 kVA, 125 kVA and above 125 kVA (but up to 250 kVA) respectively.
b) Foundation Mounted Substations
For transformers of capacity above 250 kVA the transformers are too heavy for pole mounting..
<number>
Notes: <number>

## Slide 13
A substation has several equipments which are briefly discussed below:
Bus-bars
Bus bars are the conductors to which a number of incoming and outgoing circuits are connected.
Power Transformer
Power transformer is used to step-up or step-down the voltage and transfer power from one A.C voltage to another A.C voltage at the same frequency under all currents and also at short circuit condition.
Circuit Breaker
Circuit breaker is an automatic switching device which can make and break an electric circuit under normal current and short circuit condition.
Isolators
Isolator is a disconnecting switch which is used for disconnecting a circuit under no-load condition.
Substation Equipment and Their Functions
<number>
Notes: <number>

## Slide 14
Earthing Switch
Earthing switch is connected between the line conductor and the earth. Under normal condition it is open. When line is disconnected, the earthing switch is closed to discharge the voltage on dead lines to earth.
Current Transformer
Current transformer is used to step-down currents for measurement, protection and control purposes.
Voltage Transformer
Voltage transformer is used to step-down voltage for measurement, protection and control purpose.
Lightning Arrester (Surge Arrester)
Lightning arrester is connected between phase and ground at the substation to discharge lightning over-voltages and switching over- voltages to earth.
<number>
Notes: <number>

## Slide 15
Shunt Reactor
Shunt reactor is used to control voltage during low load periods and compensate shunt capacitance of transmission line. It is used in EHV substations particularly.
Series Reactor
Series reactor is used to reduce the short-circuit current or starting currents.
Neutral-Grounding Resistor
Neutral-grounding resistor is used to limit the earth fault current.
Shunt Capacitors
Shunt capacitors are used for power factor improvement, switched in during low power factor loads , in particular.
<number>
Notes: <number>

## Slide 16
Series Capacitors
They are used for compensation of series reactance of long lines and sometimes for power factor improvement also.
Control Cabling
It is used for protective circuits, control circuits, metering circuits and communication circuits .
Power Cables
They are used to provide supply path to various auxiliary equipment and machines.
PLCC System (Power Line Carrier Communication System)
It is used for communication, telemetry tele-control power line carrier protection etc.
DC Batteries Sets & Battery Chargers
They are used to provide auxiliary low voltage DC supply for the protective devices.
<number>
Notes: <number>

## Slide 17
There are several ways in which the switching equipment can be connected in the electrical layout of generating station, receiving station or a switchgear in a distribution system.
Single Bus-bar Design
This simple arrangement consists of a single (three-phase) bus-bar to which the various feeders are connected. In case of a fault or maintenance of a bus-bar the entire bus-bar has to be de-energized and the total shutdown results, shown in Figure below.
Bus-Bar Arrangements in Switchyards
<number>
Notes: <number>

## Slide 18
Figure Single Bus-bar Design.
<number>
Notes: <number>

## Slide 19
Duplicate Bus-bar Design
The duplicate or double bus-bar system provides additional flexibility, continuity of supply and permits periodic maintenance without total shutdown. In the event of fault on one bus the other can be used.
Figure given below shows the duplicate bus-bar arrangement in a generating station. Each generator has only one circuit breaker and between the circuit breaker and each bus-bar there is one isolator.
There are two buses called main bus and reserve bus. The coupler can be closed so as to connect the two buses. The double bus scheme has been used in important 132 kV substations.
<number>
Notes: <number>

## Slide 20
Figure Duplicate Bus-bar System.
<number>
Notes: <number>

## Slide 21
While transferring the power to the reserve bus, the following steps may be taken:
Close tie circuit breaker i.e. bus coupler. The two buses are now at same potential.
Close isolators on reserve bus.
Open isolators on main bus.
The power is now transferred to the reserve bus and main bus is disconnected. In more important stations, two circuit breakers are used per generator, one for each bus.
For 400 kV Switchyards two Main Buses plus one transfer bus scheme is preferred. The transfer bus is used for transferring power from Main Bus I to Main Bus II.
<number>
Notes: <number>

## Slide 22
Figure Sectionalizing of Bus.
Sectionalization of Bus
Sectionalizing the buses has added advantages. One section can be completely shut down for maintenance and repairs while the other continues to Supply, as shown in Figure below. Secondly by adding a current limiting reactor between the sections, the fault MVA can be reduced, thereby circuit breaker of lesser capacity may be permitted.
<number>
Notes: <number>

## Slide 23
Ring Bus
Ring bus provides greater flexibility. The supply can be taken from any adjacent section. The effect of fault in one section is localized to that section alone. The other section continues to operate, as shown in the Figure below.
Figure . Rings Bus.
<number>
Notes: <number>

## Slide 24
One and a half Breaker Design
One-and-a-half breaker arrangement needs three circuit breakers for two circuits. Any circuit breaker can be switched-off for the purpose of maintenance, without the provision of bypass.
The number of circuit breaker per circuits 1½ hence the name.
In 1½ breaker ar­rangement, circuit I and circuit II can take supply either from bus bar I or bus-bar II.
Thus this arrangement gives high security against loss of supply. Such arrangement is particularly suitable for the switchyards in large generating stations in which very high power is to be handled by individual circuits.
<number>
Notes: <number>

## Slide 25
Figure. One and a half Circuit Breaker Arrangement.
<number>
1½ Breaker arrangement uses 1½ circuit breaker per circuit. The higher cost is justified because of higher security and by passing facility obtained. The 1½ circuit-breaker arrangement has been used in important 500 kV substations.
Notes: <number>

## Slide 26
Mesh Arrangement
Another method of economic use of circuit breakers in a substation is mesh-arrangement, see Figure given in next slide.
In mesh arrangement, the circuit breakers are installed in the mesh formed by the buses.
The circuits are tapped from the node points of the mesh. In the figure shown, four circuit breakers are utilized to control eight circuits.
In the event of a fault on any circuit, two circuit breakers have to open, resulting in opening of the mesh.
<number>
Notes: <number>

## Slide 27
Figure . Mesh Arrangement (Only four circuit breakers control eight circuits).
<number>
Notes: <number>

## Slide 28
The main elements of the installations; circuit breakers, isolators, fuses, instrument transformers, power transformers etc. are represented by standard graphical symbols on the single line diagrams.
A balanced three-phase system is solved as a single-phase circuit made of one line and the neutral return.
Standard symbols are used to indicate the various components. The simplified one-line diagram is called the single-line diagram.
A further advantage of the one-line diagram is in the power flow studies.
From the one-line diagram the impedance, or reactance, diagram can be conveniently developed.
Single Line Representation of Power systems
<number>
Notes: <number>

## Slide 29
Power System Components and their equivalent symbols.
<number>
Notes: <number>

## Slide 30
<number>

## Slide 31
A single line diagram showing the sequence and location of different components and equipments is given below.
Figure: Substation with Interconnection of different components.
<number>
Notes: <number>

## Slide 32
<number>
A One-Line Diagram of a Portion of a Power System
The components are: generators, circuit breakers, transformers, transmission lines, and loads.

## Slide 33: Equivalent Circuit and Impedance Diagram
The equivalent circuit of the components will be done based on the following assumption
A generator can be represented by a voltage source in series with an inductive reactance. The internal resistance of the generator is negligible compared to the reactance.
The motor load is inductive.
The static load has a lagging power factor.
A transformer is represented by a series impedance on a per phase basis.
The transmission line is of medium length and can be represented by a T section.
<number>

## Slide 34: Equivalent Circuit and Impedance Diagram
<number>
Fig 1(a) Impedance Diagram

## Slide 35: Equivalent Circuit and Reactance Diagram
Fig 1(b) Corresponding Reactance Diagram

## Slide 36: Example
Show the one-line diagram of a simple power system that has two generators, one grounded through a reactor and one through a resistor, are connected to a bus and through a step-up transformer to a transmission line. Another generator, grounded through a reactor, is connected to a bus and through a transformer to the opposite end of the transmission line. A load is connected to each bus.

## Slide 37: Solution
Single line diagram

## Slide 38
Equivalent circuit and impedance diagram