## Slide 1: Debre Markos University Debre Markos Institute of Technology
School of Electrical and computer Engineering
Introduction to Power system
4. Characteristics and parameters of transmission lines

## Slide 2: Transmission line Parameters
The transmission of electric power is done by 3-phase, 3- wire overhead lines.
An A.C. transmission line has resistance, inductance and capacitance uniformly distributed along its length. These are known as constants or parameters of the line.
The performance of a transmission line depends to a considerable extent upon these constants.
For instance, these constants determine whether the efficiency and voltage regulation of the line will be good or poor.
<number>

## Slide 3: Typical single-circuit lines and double-circuit lines in horizontal, triangular and vertical arrangements.
<number>

## Slide 4
Fig 4.1 (i) (ii)
Resistance: It is the opposition of line conductors to current flow. The resistance is uniformly distributed along the whole length of the line as shown in Fig4.1(i).
However, the performance of a transmission line can be analyzed conveniently if distributed resistance is considered as lumped as shown in Fig. 4.1(ii).
Inductance: When an alternating current flows through a conductor, a changing flux is set up which links the conductor.
Due to these flux linkages, the conductor possesses inductance.
<number>

## Slide 5
Mathematically, inductance is defined as the flux linkages per ampere. i.e Inductance,
The inductance is also uniformly distributed along the length of the line as show in Fig. 4.1(i).
Again for the convenience of analysis, it can be taken to be lumped as shown in Fig. 4.1(ii).
Capacitance: is an electronic component that stores electric charge.
The capacitor is made of 2 close conductors (usually plates) that are separated by a dielectric material.
<number>
Notes: <number>

## Slide 6
We know that any two conductors separated by an insulating material constitute a capacitor.
As any two conductors of an overhead transmission line are separated by air which acts as an insulation, therefore, capacitance exists between any two overhead line conductors.
The capacitance between the conductors is the charge per unit potential difference. Capacitance,
Where, q = charge on the line in coulomb
v = p.d. between the conductors in volts
<number>

## Slide 7
The capacitance is uniformly distributed along the whole length of the line and may be regarded as a uniform series of capacitors connected between the conductors as shown in Fig. 4.2(i).
Fig 4.2 (i) (ii)
<number>

## Slide 8: Resistance of a Transmission Line
The resistance of transmission line conductors is the most important cause of power loss in a transmission line.
The AC resistance of a conductor in a transmission line is based on the calculation of its DC resistance.
If DC current is flowing along a round cylindrical conductor, the current is uniformly distributed over its cross-section area and its DC resistance is evaluated by,
where ρ - is the resistivity of conductor
l - is the length and
A - is the cross-sectional area
<number>

## Slide 9
If AC current is flowing, rather than DC current, the following factors need to be considered:
  1. Frequency or skin effect
  2.Temperature
  3. Proximity effect
  4. Spiraling and Bundle Conductor Effect
<number>

## Slide 10: i) Skin Effect
When a conductor is carrying steady direct current (d.c.), this current is uniformly distributed over the whole X-section of the conductor.
However, an alternating current flowing through the conductor does not distribute uniformly, rather it has the tendency to concentrate near the surface of the conductor as shown in Fig. 4.3. This is known as skin effect.
The tendency of alternating current to concentrate near the surface of a conductor is known as skin effect.
Fig 4.3
<number>
Notes: <number>

## Slide 11
The frequency of the AC voltage produces a second effect on the conductor resistance due to the non - uniform distribution of the current. This phenomenon is known as skin effect.
As frequency increases, the current tends to go toward the surface of the conductor and the current density decreases at the center.
The skin effect depends upon the following factors :
  Nature of material
  Diameter of wire − increases with the diameter of wire.
  Frequency − increases with the increase in frequency.
  Shape of wire − less for stranded conductor than the solid conductor.
<number>

## Slide 12
Due to skin effect, the effective area of cross-section of the conductor through which current flows is reduced. Consequently, the resistance of the conductor is slightly increased when carrying an alternating current.
It may be noted that skin effect is negligible when the supply frequency is low (< 50 Hz) and conductor diameter is small (< 1cm).
A skin correction factor k, obtained by differential equations and Bessel functions, is considered to reevaluate the AC resistance.
For 60 Hz, k is estimated around 1.02.
<number>

## Slide 13: ii) Temperature Effect
The resistivity of any conductive material varies linearly over an operating temperature, and therefore, the resistance of any conductor suffers the same variations.
As temperature rises, the conductor resistance increases linearly, over normal operating temperatures, according to the following equation:
Where
  R2 is the resistance at second temperature t2
  R1 is the resistance at initial temperature t1
  T is the temperature coefficient for the particular material (C°)
<number>

## Slide 14
Resistivity () and temperature coefficient (T) constants depend upon the particular conductor material.
Table 1 lists resistivity and temperature coefficients of some typical conductor materials
<number>

## Slide 15: iii) Spiraling and Bundle Conductor Effect
There are two types of transmission line conductors: overhead and underground.
Overhead conductors
  made of naked metal and suspended on insulators,
  are preferred over underground conductors because of the lower cost and easy maintenance.
  use aluminum conductors, because of the lower cost and lighter weight compared to copper conductors,
  although more cross-section area is needed to conduct the same amount of current.
There are different types of commercially available aluminum conductors:
  Aluminum-conductor-steel-reinforced (ACSR),
  Aluminum-conductor-alloy-reinforced (ACAR),
  All-aluminum-conductor (AAC), and
  All-aluminum alloy- conductor (AAAC).
<number>

## Slide 16
ACSR is one of the most used conductors in transmission lines.
It consists of alternate layers of stranded conductors, spiraled in opposite directions to hold the strands together, surrounding a core of steel strands.
The purpose of introducing a steel core inside the stranded aluminum conductors is to obtain a high strength-to-weight ratio.
A stranded conductor offers more flexibility and easier to manufacture than a solid large conductor.
However, the total resistance is increased because the outside strands are larger than the inside strands on account of the spiraling.
<number>

## Slide 17: iv) Proximity effects
In a transmission line there is a non-uniformity of current distribution caused by a higher current density in the elements of adjacent conductors nearest each other than in the elements farther apart. The phenomenon is known as proximity effect.
It is present for three-phase as well as single-phase circuits. For the usual spacing of overhead lines at 60 Hz, the proximity effect is neglected.
Example 1:
A solid cylindrical aluminum conductor 25 km long has a diameter of 1.4732 cm. Obtain the conductor resistance at:
  50°C (b) 20°C
  The resistivity of aluminum at 20° is 2.8 x 10-8Ωm.
<number>

## Slide 18
Solution:
<number>

## Slide 19: Example 2
A three phase transmission line is designed to deliver 190.5 MVA at 220 kV over a distance of 63 km. the total transmission loss is not to exceed 2.5 percent of the rated line MVA. If the resistivity of the conductor material at 20° is 2.8 × 10−8Ωm , determine the required conductor diameter and the conductor size in circular miles.
<number>

## Slide 20: Solution
The total transmission line loss is
<number>

## Slide 21: Flux Linkages
As stated earlier, the inductance of a circuit is defined as the flux linkages per unit current.
Therefore, in order to find the inductance of a circuit, the determination of flux linkages is primary importance.
We shall discuss two important cases of flux linkages.
  Flux linkages due to internal flux
  Flux linkages due to external flux
<number>

## Slide 22
  Flux linkages due to a single current carrying conductor
Consider a long straight cylindrical conductor of radius r metres and carrying a current I amperes (r.m.s.) as shown in Fig. 4.4 (i).
This current will set up magnetic field.
The magnetic lines of force will exist inside the conductor as well as outside the conductor.
Both these fluxes will contribute to the inductance of the conductor.
<number>

## Slide 23: (i) Flux linkages due to internal flux
Refer to Fig. 4.4 (ii) where the X-section of the conductor is shown magnified for clarity. The magnetic field intensity at a point x meters from the center is given by;
Fig 4.4 (i) (ii)
<number>

## Slide 24
Assuming a uniform current density,
If μ (= μ0μr ) is the permeability of the conductor, then flux density at the considered point is given by;
<number>

## Slide 25
This flux links with current only. Therefore, flux linkages per metre length of the conductor is
<number>

## Slide 26: ii) Flux linkages due to external flux
Now let us calculate the flux linkages of the conductor due to external flux.
The external flux extends from the surface of the conductor to infinity. Referring to Fig. 4.5, the field intensity at a distance x meters (from center) outside the conductor is given by ;
Fig. 4.5
<number>

## Slide 27
<number>

## Slide 28: Inductance of a Single Phase Two-wire Line
A single phase line consists of two parallel conductors which form a rectangular loop of one turn.
When an alternating current flows through such a loop, a changing magnetic flux is set up.
The changing flux links the loop and hence the loop (or single phase line) possesses inductance.
It may appear that inductance of a single phase line is negligible because it consists of a loop of one turn and the flux path is through air of high reluctance.
But as the X -sectional area of the loop is very large, even for a small flux density, the total flux linking the loop is quite large and hence the line has appreciable inductance.
Consider a single phase overhead line consisting of two parallel conductors A and B spaced d meters apart as shown in Fig. 4.6.
<number>

## Slide 29
Conductors A and B carry the same amount of current (i.e. IA = IB), but in the opposite direction because one forms the return circuit of the other.
∴ IA + IB = 0
Fig. 4.6
In order to find the inductance of conductor A (or conductor B), we shall have to consider the flux linkages with it.
There will be flux linkages with conductor A due to its own current IA and also due to the mutual inductance effect of current IB in the conductor B.
………………...(ii)
<number>
Notes: <number>

## Slide 30
<number>

## Slide 31
<number>

## Slide 32
Note that
eq.(ii) is the inductance of the two-wire line and is sometimes called loop inductance.
However, inductance given by eq.(i) is the inductance per conductor and is equal to half the loop inductance.
Expression in alternate form. The expression for the inductance of a conductor can be put in a concise form.
<number>

## Slide 33
The radius r′ is that of a fictitious conductor assumed to have no internal flux but with the same inductance as the actual conductor of radius r. The quantity e−1/4 = 0·7788 so that
The term r′ (= r e−1/4) is called geometric mean radius (GMR) of the wire. Note that eq. (iii) gives the same value of inductance LA as eq. (i).
The difference is that eq. (iii) omits the term to account for internal flux but compensates for it by using an adjusted value of the radius of the conductor.
<number>

## Slide 34: 4.6 Inductance of a 3-Phase Overhead Line
Fig. 4.7 shows the three conductors A, B and C of a 3-phase line carrying currents IA, IB and IC respectively.
Let d1, d2 and d3 be the spacing's between the conductors as shown.
Let us further assume that the loads are balanced i.e. IA + IB + IC = 0.
Consider the flux linkages with conductor A.
There will be flux linkages with conductor A due to its own current and also due to the mutual inductance effects of IB and IC.
Fig 4.7
<number>

## Slide 35
<number>

## Slide 36
Symmetrical spacing
If the three conductors A, B and C are placed symmetrically at the corners of an equilateral triangle of side d, then, d1 = d2 = d3 = d. Under such conditions, the flux linkages with conductor A become :
<number>

## Slide 37
<number>

## Slide 38: (ii) Unsymmetrical spacing.
When 3-phase line conductors are not equidistant from each
other, the conductor spacing is said to be unsymmetrical.
Under such conditions, the flux linkages and inductance of each phase are not the same.
A different inductance in each phase results in unequal voltage drops in the three phases even if the currents in the conductors are balanced.
Therefore, the voltage at the receiving end will not be the same for all phases.
<number>
Notes: <number>

## Slide 39
In order that voltage drops are equal in all conductors, we generally interchange the positions of the conductors at regular intervals along the line so that each conductor occupies the original position of every other conductor over an equal distance.
Such an exchange of positions is known as transposition, Fig. 4.8 shows the transposed line.
<number>
Notes: <number>

## Slide 40
The phase conductors are designated as A, B and C and the positions occupied are numbered 1, 2 and 3.
The effect of transposition is that each conductor has the same average inductance.
Fig 4.8 shows a3-phase transposed line having unsymmetrical spacing.
<number>

## Slide 41
Let us assume that each of the three sections is 1 m in length.
Let us further assume balanced conditions i.e., IA + IB +IC = 0.
Let the line currents be :
IA = I (1+ j 0)
IB = I (− 0·5 − j 0·866)
IC = I (− 0·5 + j 0·866)
<number>

## Slide 42
As proved above, the total flux linkages per meter length of conductor A is
<number>

## Slide 43
132 kV surge arrestors
Oil pump
<number>
Notes: <number>

## Slide 44
<number>

## Slide 45
If we compare the formula of inductance of an unsymmetrical spaced transposed line with that of symmetrically spaced line, we find that inductance of each line conductor in the two cases will be equal if .
The distance d is known as equivalent equilateral spacing for unsymmetrical transposed line.
<number>

## Slide 46: 4.7 Concept of Self-GMD and Mutual-GMD
The use of self geometrical mean distance (abbreviated as self-GMD) and mutual geometrical mean distance (mutual-GMD) simplifies the inductance calculations
The symbols used for these are respectively Ds and Dm. We shall briefly discuss these terms.
(i) Self-GMD (Ds) In order to have concept of self-GMD (also sometimes called Geometrical mean radius ; GMR),
<number>

## Slide 47
In this expression, the term 2 × 10-7 × (1/4) is the inductance due to flux within the solid conductor.
For many purposes, it is desirable to eliminate this term by the introduction of a concept called self-GMD or GMR.
If we replace the original solid conductor by an equivalent hollow cylinder with extremely thin walls, the current is confined to the conductor surface and internal conductor flux linkage would be almost zero.
Consequently, inductance due to internal flux would be zero and the term 2 × 10-7 × (1/4) shall be eliminated.
The radius of this equivalent hollow cylinder must be sufficiently smaller than the physical radius of the conductor to allow room for enough additional flux to compensate for the absence of internal flux linkage.
<number>

## Slide 48
It can be proved mathematically that for a solid round conductor of radius r, the self-GMD or GMR = 0·7788 r. Using self-GMD, the eq. (i) becomes :
It may be noted that self-GMD of a conductor depends upon the size and shape of the conductor and is independent of the spacing between the conductors.
<number>

## Slide 49: (ii) Mutual-GMD
The mutual-GMD is the geometrical mean of the distances form one conductor to the other and, therefore, must be between the largest and smallest such distance. In fact, mutual-GMD simply represents the equivalent geometrical spacing.
(a) The mutual-GMD between two conductors (assuming that spacing between conductors is large compared to the diameter of each conductor) is equal to the distance between their centres i.e.
Dm = spacing between conductors = d
(b) For a single circuit 3-φ line, the mutual-GMD is equal to the equivalent equilateral spacing i.e., (d1 d2 d3)1/3.
Dm = (d1 d2 d3)1/3
<number>

## Slide 50
(c) The principle of geometrical mean distances can be most profitably employed to 3-φ double circuit lines. Consider the conductor arrangement of the double circuit shown in Fig. 4.9. Suppose the radius of each conductor is r.
Fig 4.9
<number>

## Slide 51
Self-GMD of conductor = 0·7788 r
Self-GMD of combination aa´ is
Ds1 = (Daa × Daa′× Da′a′× Da′a)1/4
  Daa or Da′a′ means self-GMD of the conductor. Daa′ means distance between a and a′
Self-GMD of combination bb´ is
Ds2 = (Dbb × Dbb′ × Db′b′× Db′b)1/4
Self-GMD of combination cc′ is
Ds3 = (Dcc × Dcc′ × Dc′c′ × Dc′c)1/4
Equivalent self-GMD of one phase
Ds = (Ds1 × Ds2 × Ds3)1/3
The value of Ds is the same for all the phases as each conductor has the same radius.
Mutual-GMD between phases A and B is
<number>

## Slide 52
DAB = (Dab × Dab′× Da′b × Da′b′)1/4
Mutual-GMD between phases B and C is
DBC = (Dbc × Dbc′× Db′c × Db′c′)1/4
Mutual-GMD between phases C and A is
DCA = (Dca × Dca′× Dc′a × Dc′a′)1/4
Equivalent mutual-GMD, Dm = (DAB × DBC × DCA)1/3
It is worthwhile to note that mutual GMD depends only upon the spacing and is substantially independent of the exact size, shape and orientation of the conductor.
<number>

## Slide 53: 4.8 Inductance Formulas in Terms of GMD
<number>

## Slide 54: 4.9 Electric Potential
The electric potential at a point due to a charge is the work done in bringing a unit positive charge from infinity to that point.
The concept of electric potential is extremely important for the determination of capacitance in a circuit since the latter is defined as the charge per unit potential.
We shall now discuss in detail the electric potential due to some important conductor arrangements.
Fig 4.10
<number>

## Slide 55: (i) Potential at a charged single conductor.
Consider a long straight cylindrical conductor A of radius r metres.
Let the conductor operate at such a potential (VA) that charge QA coulombs per metre exists on the conductor.
It is desired to find the expression for VA. The electric intensity E at a distance x from the centre of the conductor in air is given by:
where,
<number>

## Slide 56
As x approaches infinity, the value of E approaches zero. Therefore, the potential difference between conductor A and infinity distant neutral plane is given by :
<number>

## Slide 57: 4.10 Capacitance of a Single Phase Two-wire Line
Consider a single phase overhead transmission line consisting of two parallel conductors A and B spaced d meters apart in air.
Suppose that radius of each conductor is r meters. Let their respective charge be + Q and − Q coulombs per meter length.
Fig 4.11
<number>

## Slide 58
The total p.d. between conductor A and neutral “infinite” plane is
Both these potentials are w.r.t. the same neutral plane. Since the unlike charges attract each other, the potential difference between the conductors is
<number>

## Slide 59
<number>

## Slide 60: 4.11Capacitance of a 3-Phase Overhead Line
In a 3-phase transmission line, the capacitance of each conductor is considered instead of capacitance from conductor to conductor. Here, again two cases arise viz.,
  symmetrical spacing
  unsymmetrical spacing.
(i) Symmetrical Spacing.
Fig. 4.12 shows the three conductors A, B and C of the 3-phase overhead transmission line having charges QA, QB and QC per metre length respectively.
Let the conductors be equidistant (d metres) from each other. We shall find the capacitance from line conductor to neutral in this symmetrically spaced line.
Referring to Fig. 4.12, overall potential difference between conductor A and infinite neutral plane is given by
<number>

## Slide 61
Fig 4.12
<number>

## Slide 62
(ii) Unsymmetrical spacing.
Fig. 4.13 shows a 3-phase transposed line having unsymmetrical spacing. Let us assume balanced conditions i.e. QA + QB + QC = 0.
<number>

## Slide 63
Fig. 4.13
<number>

## Slide 64
<number>

## Slide 65
Corona
<number>

## Slide 66: Introduction
When an alternating potential difference is applied across two conductors whose spacing is large as compared to their diameters, there is no apparent change in the condition of atmospheric air surrounding the wires if the applied voltage is low.
The phenomenon of violet glow, hissing noise, production of ozone gas, power loss and radio interference in an overhead transmission line is known as corona.
<number>

## Slide 67: Theory of corona formation
Some ionization is always present in air due to cosmic rays, ultraviolet radiations and radioactivity.
Therefore, under normal conditions, the air around the conductors contains some ionized particles (i.e., free electrons and +ve ions) and neutral molecules.
When p.d. is applied between the conductors, potential gradient is set up in the air which will have maximum value at the conductor surfaces.
<number>

## Slide 68
Under the influence of potential gradient, the existing free electrons acquire greater velocities.
The greater the applied voltage, the greater the potential gradient and more is the velocity of free electrons.
When the potential gradient at the conductor surface reaches about 30 kV per cm (max. value),the velocity acquired by the free electrons is sufficient to strike a neutral molecule with enough force to dislodge one or more electrons from it.
<number>

## Slide 69
This produces another ion and one or more free electrons, which is turn are accelerated until they collide with other neutral molecules, thus producing other ions.
Thus, the process of ionization is cummulative. The result of this ionization is that either corona is formed or spark takes place between the conductors.
<number>

## Slide 70: Factors Affecting Corona
The following are the factors upon which corona depends :
  Atmosphere: As corona is formed due to ionization of air surrounding the conductors, therefore, In the stormy (rainy) weather, the number of ions is more than normal and as such corona occurs at much less voltage as compared with fair weather.
  Conductor size: The rough and irregular surface will give rise to more corona because unevenness of the surface decreases the value of breakdown voltage.
<number>

## Slide 71
  Spacing between conductors: If the spacing between the conductors is made very large as compared to their diameters, there may not be any corona effect. It is because larger distance between conductors reduces the electro-static stresses at the conductor surface, thus avoiding corona formation.
  Line voltage: The line voltage greatly affects corona. If it is low, there is no change in the condition of air surrounding the conductors and hence no corona is formed.
<number>

## Slide 72
However, if the line voltage has such a value that electrostatic stresses developed at the conductor surface make the air around the conductor conducting, then corona is formed.
<number>

## Slide 73: Advantages and Disadvantages of Corona
Corona has many advantages and disadvantages.
Advantages
(i) Due to corona formation, the air surrounding the conductor becomes conducting and hence virtual diameter of the conductor is increased. The increased diameter reduces the electrostatic stresses between the conductors.
(ii) Corona reduces the effects of transients produced by surges.
<number>

## Slide 74: Disadvantages
(i) Corona is accompanied by a loss of energy. This affects the transmission efficiency of the line.
(ii) Ozone is produced by corona and may cause corrosion of the conductor due to chemical action.
(iii) The current drawn by the line due to corona is non-sinusoidal and hence non-sinusoidal voltage drop occurs in the line. This may cause inductive interference with neighboring communication lines.
<number>

## Slide 75: Methods of Reducing Corona Effect
It has been seen that intense corona effects are observed at a working voltage of 33 kV or above.
Therefore, careful design should be made to avoid corona on the sub-stations or bus-bars rated for 33 kV and higher voltages otherwise highly ionized air may cause flash-over in the insulators or between the phases, causing considerable damage to the equipment.
The corona effects can be reduced by the following methods :
<number>

## Slide 76
(i) By increasing conductor size: By increasing conductor size, the voltage at which corona occurs is raised and hence corona effects are considerably reduced.
This is one of the reasons that ACSR conductors which have a larger cross-sectional area are used in transmission lines.
(ii) By increasing conductor spacing: By increasing the spacing between conductors, the voltage at which corona occurs is raised and hence corona effects can be eliminated.
However, spacing cannot be increased too much otherwise the cost of supporting structure (e.g., bigger cross arms and supports) may increase to a considerable extent.
<number>